## NS check sheet
NS-Type JOINT ASSEMBLING CHECK SHEET |  |  |  | Approved by | Recorded by
1st Edition (Apr.2021)
Pipe size (in.) | OD(mm) | #N/A | #N/A
Crew/Contractor |  |  | Project/Site
Date
STA.
Item No.
Description
Symbol
Remark
Check List
1. Back-up Ring position
2. Insertion position
3. Clearance between Spigot and Socket should be even (4 points)
4. Torque up (75ft.lbs≒100N-m)
5. Bolting balance (inch) Gap shall be uniform all around. Allowable difference is less than 1/4". | Top
South
Bottom
North
Judge
6. Rubber Gasket shape | Top
South
Bottom
North
Judge
7.Length between bell and white line (inch) Deflection angle shall be less than allowable degrees. | Top
South
Bottom
North
Allowable | Deflection (Hor.)
#N/A | Deflection (Ver.)
Judgement
Note

## Appendix
1. Back-up Ring position | 2. Insertion pattern
Align the center of the red lines a split portion
of Lock ring
6. Combination of A and C is bad.
( >1/4”) (0 - 1/4”) ( <0)
Rim
Back-up Ring
Rubber gasket
Back-up Ring
Red Lines
Split Portion
Split Portion
Lock Ring
Pipe
Two white Lines
Pipe with Liner
Marking
Fitting
Marking
Bad
Gasket on gland

## Source (hidden)
Pipe size |  | OD | tolerance | Allowable def.
Inch | mm | mm | mm | deg.
20 | 500 | 528 | ±2.0 | 3.3333
24 | 600 | 630.8 | ±2.0 | 2.8333
28 | 700 | 733 | +2, -3 | 2.5
32 | 800 | 836 | +2, -3 | 2.1667
36 | 900 | 939 | +2, -3 | 2
40 | 1000 | 1041 | +2, -3 | 1.8333