## S-Check sheet
S-Type JOINT ASSEMBLING CHECK SHEET |  |  |  |  | Approved by | Recorded by
1st Edition (Apr.2021)
Pipe size (in.) |  | OD(mm) | #N/A | +2,-4
Crew/Contractor |  |  |  | Project/Site
Date
STA.
Item No.
Description
Symbol
Remark
Check List
1.Gap of Connecting Piece Ⅲ (1.5mm to 2.0mm (approx.1/16"))
2.Clearance between Lock Ring and Spigot (<1mm)
3.Clearance between Spigot and Socket should be even (4 points)
4.Back-up Ring position
5.Split Ring position
6.Torque up (150ft.lbs≒200N-m)
7.Bolting balance (inch) Gap shall be uniform all around. Allowable difference is less than 1/4". |  | Top
Right
Bottom
Left
Judge
8.Rubber Gasket shape |  | Top
Right
Bottom
Left
Judge
9.Gap of Y (inch) Deflection angle shall be less than allowable degrees. |  | Top
Right
Bottom
Left
Allowable | Deflection(Hor.)
#N/A | Deflection(Ver.)
Joint Test | Date
Final pressure
Judgement
Note

## Appendix
①Clean both the socket and the spigot. | ⑥The metal part faces to the spigot
②Gap shall be 1.5mm to 2.0mm (approx.1/16").
⑨Combination of A and C is bad.
③Lock Ring holds the spigot tightly.
④Lubricate the socket and the spigot with appropriate
lubricant for ductile iron pipe.
⑤Place the split portion at the bottome.
Gap of Connecting Piece Ⅲ
Metal plate
Back-up Ring
( >1/4”) (0 - 1/4”) ( <0)

## OD (hidden)
|  | D2 | 許容差 | 許容曲げ角度
44 | 1100 | 1144 | +2, -4 | 1.6667
48 | 1200 | 1246 | +2, -4 | 1.5
54 | 1350 | 1400 | +2, -4 | 1.5
60 | 1500 | 1554 | +2, -4 | 1.5
66 | 1650 | 1701 | +2, -4 | 1.5
72 | 1800 | 1848 | +2, -4 | 1.5
104 | 2600 | 2684 | +2, -4 | 1.5